## Slide 1
All descriptions illustrations, and specifications in this brochure should be considered approximate and may relate to optional equipment or feature
Quick User Guide
MorphoWave Compact

## Slide 2: MorphoWave Compact box content
Product packaging checklist:
QTY | ITEM
1 | MorphoWave Compact terminal
1 | Wall Mounting Plate
1 | Documentation package
Electronic documentation is provided in Adobe® Acrobat® format (PDF). Adobe® Acrobat® Reader is available at http://www.adobe.com.

## Slide 3
Regulatory, safety and environmental notices
Products bearing the CE marking comply with one or more of the following EU Directives as may be applicable:
Radio Equipment Directive (RED) 2014/53/UE
RoHS Directive 2011/65/EU.
Compliance with these directives is assessed using applicable European Harmonised Standards.<<<
The installation of this product should be made by a qualified service Person and should comply with all local regulations.
It is strongly recommended to use a class II power supply at 12V-24V and 2.5 A. min (at 12V) in conformity with Safety Electrical Low Voltage (SELV). The AC power supply cable length should not exceed 10 meters.
This system must be installed in accordance with the National Electrical Code (NFPA 70), and the local authority having jurisdiction.
This product is intended to be installed with a power supply complying with IEC60950-1, in accordance with the NEC Class 2 requirements; or supplied by a listed IEC60950-1 external Power Unit marked Class 2, Limited Power source, or LPS and rated 12VDC, 2.5 A minimum or 24VDC, 1.25 A minimum.
In case of building-to-building connection it is recommended to connect 0V to ground. Ground cable must be connected with the terminal block Power Ground.
Note that all connections of the MorphoWave Compact terminal described hereafter are of SELV (Safety Electrical Low Voltage) type.
This symbol means do not dispose of your product with your other household waste. Instead, you should protect human health and the environment by handing over your waste equipment to a designated collection point for the recycling of waste electrical and electronic equipment.

## Slide 4: Table of Contents
Color | Step | Content
 | One | Overview
 | Two | Wiring
 | Three | Communication
 | Four | SDAC (Single Door Access Control)
 | Five | Administration
 | Six | Software
 | Seven | Enrollment
 | Eight | Optional features

## Slide 5: Product Overview
MorphoWave Compact provides an innovative and effective solution for access control applications using very fast acquisitions of four (4) fingerprints without any contact.
Step one : overview
    Access control and Time & Attendance
    Biometric authentication by a hand swipe through the active volume without contact
    IDEMIA False finger detection algorithms
    Simple and ergonomic man-machine interface
    Contactless card reader (MIFARE Classic, MIFARE Plus, DESFire, HID® Iclass*, HID® PROX*)
    Intercom system
    Universal connectivity (Gigabit Ethernet, Wi-FiTM, RS485/422, Wiegand, Dataclock)
    Anti-tamper sensor
* Depending on product version

## Slide 6: Terminal Implementation
To secure an access, IDEMIA recommends installing the MorphoWave Compact terminal as a part of a typical Access Control system, which consists of the components described below.
Step one : overview
The MorphoWave Compact terminal
Its role is to process the access request from the user. It performs access right checks using one-to-many biometric identification or one-to-one biometric verification, and/or RF card authentication, and/or PIN check.
A Door Electric Latch or equivalent (3rd party product)
The Access Controller sends a command to activate the latch if the access is granted (i.e. if the individual's User ID is listed in the Controller authorized user List). Control of the latch is made through a dry contact..
An Alarm (3rd party product)
The terminal sends a message to the Access Controller, to activate the Alarm as soon as a malicious activity, such as tamper or pulling, is detected
An Access Controller (3rd party product)
The terminal interfaces with an Access Controller (using TCP/IP, Wiegand, Data Clock, RS485 or RS422 protocol):
After access request, the terminal sends the result of user’s access rights to the Access Controller (this message contains at least the User ID)
The Access Controller performs additional checks, and returns the final decision (access granted/denied) to the terminal (which displays the result to the user), and to the door controller which opens the door (if the access has been granted).
B
A
B
D
D
C
C
A

## Slide 7: Typical Access Control Process
Note: One user must be enrolled in the terminal database, in order to be able to perform biometric check.
On Access Request, the terminal checks user’s access rights using a biometric check.
If the result of the check is successful (access granted), a message is sent to the Central Access Controller for additional access rights check.
If the user is allowed to access to the protected zone, the central access controller returns an "access granted" message to the terminal and a “open” command to the gate controller.

## Slide 8: Access Control Modes
The terminal can be configured in one of the modes described in the table below
 | Identification | Authentication | Multifactor | Proxy
Access control application | Application that runs on the terminal when it starts. | Application that runs on the terminal when it starts. | Application that runs on the terminal when it starts. | Remote application that controls the terminal through network commands
Access control triggering event | A user swipes his/her hand in the biometric sensor. | A user places a contactless card in front of the reader. (*) | Both Identification and Authentication triggers are enabled. | Triggering events are selected by the remote application
Biometric check (if enabled) | The user’s captured fingerprints are matched against all fingerprints in the terminal database. | The user’s captured fingerprints are matched against their reference fingerprints. (**) | As per Identification or Authentication, depending on the triggering event | Selected by the remote application
Decision to display result signal to user | By Identification standalone application or controller feedback | By Authentication standalone application or controller feedback | By running standalone application or controller feedback | By remote application
(* ) or the user enter their Identifier on the keypad, or a Wiegand frame is received from an external device
(**) stored on the contactless card or in the user record in the terminal’s local database
Step one : overview

## Slide 9: Deployment Environment
General precautions
    Do not expose the terminal to extreme temperatures.
    When the environment is very dry, avoid synthetic carpeting near the MorphoWave Compact terminal, to reduce the risk of unwanted electrostatic discharge.
Areas containing combustibles
    Do not install the terminal in the vicinity of gas stations or any other installation containing flammable or combustible gases or materials. The terminal is not designed to be intrinsically safe.
The terminal should be installed in controlled lighting conditions
    Avoid exposure of the biometric sensor to direct sunlight.
    The terminal should be installed in controlled area in order to avoid water on the sensor
Operating temperature | -10°to + 55 °C (14°to 131°F) when ECO-Mode ON -10°to + 45 °C (14°to 113°F) when ECO-Mode OFF
Operating humidity | 10 % < RH < 80 % (non condensing)
Storage temperature | -25°to + 70 °C (-13°to 158°F)
Storage humidity | 5% < RH < 95 %
Step one : overview
Please apply eco mode feature accordingly to operating temperature range in order to avoid over heating of the product

## Slide 10: ECO Mode
Step one : overview
When ECO Mode setting is OFF, the proximity sensors are disabled :
If the product enters in Stand-by mode (with ECO mode setting OFF), waving the hand will not wake-up the product (for details on ECO-MODE, please refer to next page).
On top of the standard Stand-by mode, MorphoWave Compact provides an ECO Mode
When ECO Mode setting is ON :
    green light of the sensor is switched off after 30s
    the 2 proximity sensors (on each side of the product) are activated, allowing automatic detection of the hand to switch on again the green light

## Slide 11: ECO Mode detailed diagram
Step one : overview
Eco mode ON
Eco Mode OFF
NORMAL mode
Green lightning ON
ECO mode
Green lightning OFF
STAND-BY mode
Green lightning OFF
Sensor camera OFF
Wake up :
- Hand wave
- Touchscreen action
- Contactless card detection
- Remote wake-up
Time out (fixed)
30s
Wake up :
- Hand wave
- Touchscreen action
- Contactless card detection
- Remote wake-up
Time out
selectable
from 30s to 360s
Time out
selectable
from 30s to 360s
NORMAL mode
Green lightning ON
STAND-BY mode
Green lightning OFF
Sensor camera OFF
Wake up :
- Touchscreen action
- Contactless card detection
- Remote wake-up

## Slide 12: Wiring Overview
Power supply from electrical source shall be switched off before starting the installation.
Before proceeding, make sure that the person in charge of installation and connections, is properly connected to earth, in order to prevent Electrostatic Discharges (ESD).
All connections of the terminal are of SELV (Safety Electrical Low Voltage) type.
Step two : wiring
8 wires
5 wires
7 wires
7 wires
Backup of the Date/Time of the terminal: the volatile settings (such as date/time) of the terminal are protected against power failure, by a dedicated component during a least 24 hours (at 25oC) without external power supply.
RJ-45 : Ethernet & PoE |  | 
1 | ETH TX+ | Orange / White
2 | ETH TX- | Orange
3 | ETH RX+ | Green / White
4 | ETH VPORT+ | Blue
5 | ETH VPORT+ | Blue / White
6 | ETH RX- | Green
7 | ETH VPORT- | Brown / White
8 | ETH VPORT- | Brown
Shell | ETH GND | Drain wire (no color)
Wiegand IN & Wiegand OUT |  | 
25 | WIEGAND_LEDOUT1 | Blue
28 | WIEGAND_LEDOUT2 | Blue / Red
23 | WIEGAND_IN1 | White / Red
24 | WIEGAND_OUT0 | Green
26 | WIEGAND_OUT1 | White
21 | WIEGAND_IN0 | Green / Red
27 | WIEGAND_GND | Black / Red
RS-422 and 485 |  | 
7 | RS485_RX_A | Blue / Black
8 | RS485_TX_Z | Green / White
9 | RS485_RX_B | Blue / White
10 | RS485_TX_Y | Green / Black
11 | RS485_GND | Black / Red
Power supply & Tamper switch |  | 
13 | RLY_NC | Orange / White
14 | RLY_NO | Yellow / White
12 | RLY_COM | Grey / White
5 | SWITCH_PIN1 | Light Blue
6 | SWITCH_PIN2 | Pink
1,3 | Power + 12V | Red
2,4 | Power GND | Black
7 wires
RJ45
GPIO |  | 
19 | GPI2 | Orange / Black
20 | GPO2 | Yellow / Red
17 | GPI1 | Orange / Red
18 | GPO1 | Yellow / Red
15 | GPI0 | Orange
16 | GPO0 | Yellow
22 | GPIO_GND | Black / Red
Pin numbers shown in this document correspond to the internal connector pinout in the product. The connector attached to the cable is for test only and should be removed for installation.

## Slide 13: Power supply
External Power Supply: 12-24 Volts (regulated and filtered) 2.5 Amp min @12 V, IEC/EN EN60950-1 standard compliant. If sharing power between devices, each unit must receive 2.5 A (e.g. two units would require a 12 VDC, 5 A supply).
Power Over Ethernet (POE+): power can be provided through RJ-45 connector using a PSE (Power Sourcing Equipment) IEEE802.3at type 2 compliant.
The terminal is a Class 4 (25.5 W) PD (Powered Device).
Step two : wiring
PoE+ Injector Specs
Output Voltage: 48 VDC
Output Current: 0.64 A
Power: 30 W
A battery backup or uninterrupted power supply (UPS) with built-in surge protection is recommended.
WARNING: Under powering may cause memory and data corruption; over powering may cause hardware damage. Both of these situations will void the warranty
Gauge AWG | Section (mm2) | Maximum distance (meters) vs power source rating |  | 
 |  | 12V+/-10% | 12V+/-5% | 24V+/-10%
16 | 1.31 | 9 m | 20 m | 300 m
18 | 0.82 | 6 m | 12 m | 200 m
20 | 0.52 | 3 m | 8 m | 120 m
22 | 0.32 | 2 m | 5 m | 75 m
IDEMIA recommends using a 24V power supply and AWG16 gauge cable. The voltage measured on the product block connector of the terminal must be equal to 12V-24V (-15% / +10%).
The voltage drop due to the cable shall be taken into account. The table at the right, shows the maximum distance between power supply and 1 unique device, depending on cable gauge and power supply rating.
RJ45
1-3 | Power + 12V | Red
2-4 | Power GND | Black

## Slide 14: RS-485 Communication
IMPORTANT:
A maximum of 31 devices may be installed on the same line.
The maximum total cable length is 1200m (4000 ft.)
The cable must be dedicated to this installation and not used for any other purpose
Step three : communications
RS-232 from the Com Port
RS-232 to RS-485 converter
RS-485 to 1200m (4000ft)
For RS-485 installations, the cable should be run in a daisy-chain configuration (i.e. converter > position 1 > position 2 > position 3, etc.).
Use CAT-5 UTP (or better) cable (shielded recommended) with a characteristic impedance of 120 ohms.
AWG 24 should be the minimum wire gauge used.
Choose one twisted pair of conductors to use for RS485_TX_Y (TX+, Green / Black wire - 10) and RS485_TX_Z (TX-, Green / White wire - 8). Another conductor should be used for Signal Ground (Black / Red wire - 11).
Choose a RS-232 to RS-485 converter that supports Sense Data to switch from Send to Receive mode.
8 | RS485_TX_Z (-) | Green / White
10 | RS485_TX_Y (+) | Green / Black
11 | RS485_GND | Black / Red

## Slide 15: RS-422 Communication
Step three : communications
RS-232 from the Com Port
RS-232 to RS-422 converter
RS-422 to 1200m (4000ft)
The maximum total cable length is 4000 ft. (1200m).
The cable must be dedicated to this installation and not used for any other purpose
For RS-422 installations, the cable should be run in a point to point configuration (i.e. PC > converter > terminal)
Use CAT-5 UTP (or better) cable (shielded recommended) with a impedance of 120 . AWG 24 should be the minimum wire gauge used.
Choose one twisted pair of conductors to use for RS485_TX_Y (TX+, Green / Black wire - 10) and RS485_TX_Z (TX-, Green / White wire - 8).
Choose one twisted pair of conductors to use for RS485_RX_A (RX+, Blue / Black wire - 7) and RS485_RX_B (RX-, Blue / White wire - 9).
Another conductor should be used for Signal Ground (Black / Red wire - 11).
7 | RS485_RX_A (RX+) | Blue / Black
8 | RS485_TX_Z (TX-) | Green / White
9 | RS485_RX_B (RX-) | Blue / White
10 | RS485_TX_Y (TX+) | Green / Black
11 | RS485_GND | Black / Red

## Slide 16: Ethernet and Wireless LAN
1 | ETH TX+ | Orange / White
2 | ETH TX- | Orange
3 | ETH RX+ | Green / White
4 | ETH VPORT+ | Blue
5 | ETH VPORT+ | Blue / White
6 | ETH RX- | Green
7 | ETH VPORT- | Brown / White
8 | ETH VPORT- | Brown
Shell | ETH GND | Drain wire (no color)
Step three : communications
RJ45
LAN Ethernet
Management station
Wireless
WLAN option
IDEMIA wireless enabled devices support 802.11b and 802.11g standards. WEP Open, WPA and WPA2 are supported.
Use a category 6 shielding cable (120 Ohms) or better. It is strongly recommended to insert a repeater unit every 90 m.
Static mode is enabled by default on MorphoWave Compact terminals (factory setting) : IP=192.168.1.10, Gateway=192.168.1.254, Mask= 255.255.254.0
Terminal Block Ethernet connection
    Extreme care must be taken while connecting Ethernet wire to the block board since low quality connection may strongly impact Ethernet signal sensibility.
    Connect Rx+ and Rx- with the same twisted-pair wire (and do the same with Tx+/Tx- and the other twisted-pair wire).

## Slide 17: Wiegand Communication
Step three : communications
Three-conductor cable (shielded recommended) is required for Data 0, Data 1, and WGND.
Use 18-22 AWG cable in a homerun configuration from each unit to the Access Control Panel (ACP).
    Connect WIEGAND_OUT0 (Green wire – Pin 24) to ACP Data 0,
    Connect WIEGAND_OUT1 (White wire – Pin 26) to ACP Data 1,
    Connect WIEGAND_GND (Black / Read wire – Pin 27) to ACP reader common (0vDC).
For 18 AWG, the maximum cable distance is (150m) 500 ft. ; for 20 AWG, the maximum is 90m (300 ft.) ; for 22 AWG, the maximum is 60m (200 ft.)
All controller output shall be open drain or 5 V +/- 5%
25 | WIEGAND_LEDOUT1 | Blue
28 | WIEGAND_LEDOUT2 | Blue / Red
23 | WIEGAND_IN1 | White / Red
24 | WIEGAND_OUT0 | Green
26 | WIEGAND_OUT1 | White
21 | WIEGAND_IN0 | Green / Red
27 | WIEGAND_GND | Black / Red
16 | GPO0 | Yellow
Wiegand Out
Wiegand In
LED
Out
LED In

## Slide 18: Wiegand Communication (continued)
Step three : communications
Important
By default, the Wiegand output format is not enabled. Wiegand output must be configured before connecting to the ACP.
Note
On installation, the system administrator will be prompted to select either a pre-existing Wiegand frame format or create a custom format, and upload it to the unit before the first use.
Data Clock
The Wiegand port also supports the Clock & Data protocol. The wiring is described below.
Example Format Information
Type: Standard 26-bit
Alt Site Code and Fail Site Code Range: 0-255
Template ID Number Range: 1-65535
Extended ID Number Range: N/A
ID Start Bit: 9
Length of ID: 16
Site Code Start bit: 1
Length of Site Code: 8
Start Bit length : 0
25 | WIEGAND_LEDOUT1 | Blue
28 | WIEGAND_LEDOUT2 | Blue / Red
23 | WIEGAND_IN1 | White / Red
24 | WIEGAND_OUT0 | Green
26 | WIEGAND_OUT1 | White
21 | WIEGAND_IN0 | Green / Red
27 | WIEGAND_GND | Black / Red
16 | GPO0 | Yellow
Data Clock Out
Data Clock In
LED
Out
Card present
(Legacy Morpho Mode)
Data
Clock
Clock
Data

## Slide 19: Single Door Access Control (SDAC)
If door contact is not used, GPI1 (17) and GPO1 (18) shall be connected together
Single Door Access Control (SDAC) wiring sample : with Push Button
Step four: SDAC
Power supply from electrical source shall be switched off before starting the installation.
13 | RLY_NC | Orange / White
14 | RLY_NO | Yellow / White
12 | RLY_COM | Grey / White
17 | GPI1 | Orange / Red
18 | GPO1 | Yellow / Red
15 | GPI0 | Orange
16 | GPO0 | Yellow
Power supply
Deadbolt / Door strike
Door contact
Power supply
Push Button
See details on next page for relay connection

## Slide 20: Internal Relay Wiring
RJ45
Inductive load management requires a parallel diode for a better contact lifetime.
Warning
The internal relay is limited to a maximum current of 1A @ 30V. If the deadbolt / door strike draws more than 1A, damage to the device may occur. If the deadbolt / door strike load exceeds 1A, an external relay must be used.
The internal relay is designed for 100.000 cycles. If more cycles are needed, an external relay driven by GPO must be used.
Step four: SDAC
13 | RLY_NC | Orange / White
14 | RLY_NO | Yellow / White
12 | RLY_COM | Grey / White
Power supply
VCC < 30V
Imax < 1A
Deadbolt / Door strike
Push Button on other side of the door
Protection Diode
Warning
This is recommended only for small or stand-alone applications where access control panels are not available.
In this mode it is strongly recommended to monitor the Tamper Detection of the device
Example for Normally Open connection

## Slide 21: Local Administration - First Boot Assistant
The First Boot Assistant (FBA) helps the administrator to configure all the device fundamental settings.
It is automatically launched at first terminal startup, but can also be launched on demand, though administration menu (i.e. to reinitialize terminal main settings)
Main settings managed by FBA
Date & Time & Time Zone Settings
Trigger Event: select event(s) to be processed as an access request by a user
Language Settings: user interface language selection,
Network Settings: LAN or WLAN parameters
Password Settings: terminal administration password modification
Boot assistant at next boot: Display this screen on next boot.
Step five: Administration

## Slide 22: Local Administration – Using Touch Screen Menu
Press on to access to admnisitrator menu (default security code is 12345).
For security reasons, it is highly recommended to change the devices default password to a custom password.
Step five: Administration
Frequently used icons
Exit or Go Home
Validation or confirmation
Cancel or refuse
Back (and Cancel)

## Slide 23: Administration with MorphoBioToolBox application
Terminal administration with MorphoBioToolBox (MBTB) application
Sample
Step five: Administration
The MorphoWave Compact terminal can be configured using a dedicated (Windows) application : MorphoBioToolBox
Please note that this application has an embedded User Guide (Help menu).

## Slide 24: Software for Terminal Remote Administration
MorphoWave Compact terminals are fully compatible with:
    MorphoManager application (version 13 or higher)
Step six : Software

## Slide 25: Local Enrollment Process 1/2
A new user can easily be added by using the administration menu of the MorphoWave Compact terminal.
This “local enrolment” is recommended only for small or stand alone installations or testing purposes. For professional systems enrolment should be performed remotely with an enrolment station, which is a PC with a dedicated application such as MorphoManager.
This menu allows a user’s record to be added in the local database, with the option of creating a user RF card, with the user’s reference data.
Enrolment gathering user’s data listed :
    User’s first name and last name
    User’s fingerprints (for biometric check)
    User’s administration rights (none, settings, database)
    User’s PIN (for PIN check)
    User’s duress fingerprint
    User’s access schedule and holiday schedule
    User’s dynamic message setting
    User’s record expiry date
    User to include in white list or in VIP list
    User specific access rules definition
MorphoWave Compact terminal allows you to capture up to 8 fingers per user.
Note: Refer to User enrollment section in MorphoWave Compact Administration Guide.
Step seven: capture basics

## Slide 26: Local Enrollment Process 2/2
Step seven: capture basics
NB: To complete enrollment, minimum of two waves are required.
Allow to set the quality threshold
Allow to change the current hand to enroll (left /right)

## Slide 27: Acquisition guidelines 1/2
Step seven: capture basics
Ideal acquisition procedure
Insert your hand flat, palm down, from the front of the scanner
Slightly spread apart your fingers
Place your hand between the cover and the optical sensor
Slide your hand from right to left or left to right

## Slide 28: Acquisition guidelines 2/2
Step seven: capture basics
Improper use
Do not cross your fingers
Do not place your hand with fingers spread wide
Do not place your fingers tightly together
Do not place 2 hands inside
Do not touch the cover
Do not place your hand on the optical sensor
Do not place your hand on the edge of the optical sensor
Do not tilt your hand (left to right or fingertip to palm)
Do not insert your hand fingers first from either the left or right side of the scanner

## Slide 29: Contactless Card Position – PIN input
This action is required once during the user enrolment process (generation / encoding of a user RF card), and at each authentication.
Place user’s RF card in front of embedded contactless card reader which is located behind the contactless logo.
The terminal reads the user data stored in the card (at least the User ID), and starts the authentication process, as defined by the terminal settings.
NB : Time to read all datas from the card would be more or less long depending on the quantities of datas to extract and type of card.
Contactless Card Position
Input PIN
When defined by terminal settings, the user is required to enter his PIN code, once during enrolment process, and at each authentication (in addition or instead of biometric check).
The PIN code is entered using a numeric keypad displayed on the LCD touch screen.
Step seven: capture basics
The authentication process is initiated by the detection of a user card by the contactless card reader.

## Slide 30: Time and Attendance feature
MorphoWave Compact terminals support an optional Time and Attendance (T&A) feature.
For this, the terminal adds a specific T&A information to each identification or authentication record stored in the embedded event log database.
This information is provided by the user through a specific screen displayed during identification or authentication process.
The new screen contains 4 dedicated function keys :
    Entry
    Exit
    Beginning of a task
    Ending of a task
The user is expected to press one of the keys to provide the specific Time & Attendance information to the terminal.
Depending on terminal settings, this screen is displayed before or after the user waves his/her hand in the sensor or his/her card in front of the reader.
An extended mode is also available with 16 function keys.
Step eight: optional features

## Slide 31: Recommendations
The manufacturer cannot be held responsible in case of non-compliance with the following recommendations or incorrect use of the terminal.
Repair and Accessories
    Do not attempt to repair the MorphoWave Compact terminal yourself. The manufacturer cannot be held responsible for any damage/accident that may result from attempts to repair components. Any work carried out by non-authorized personnel will void your warranty.
    Only use the terminal with its original accessories. Attempts to use unapproved accessories with your terminal will void your warranty.
Standalone terminals (not connected to a network)
    For terminals used in standalone mode, it is strongly recommended to regularly backup the local database, and at least after significant changes in the database (add, remove or modification of user’s records), on a external support such a mass storage key
Date / Time synchronization
    The MorphoWave Compact terminal clock has a +/- 10 ppm typical time deviation at +25°C (roughly +/- 1sec per day). At lower and higher temperature, deviation may be greater (maximum : 8 seconds per 48 hours).
    When the terminal is used for applications requiring high time precision, it is strongly recommended to synchronize the terminal with an external clock.
Cleaning precautions
    A dry cloth should be used to clean the terminal, especially the biometric sensor.
    The use of acid liquids, alcohol or abrasive materials is prohibited.
    Use dry air spray to remove the dust out of the sensor glass
Firmware release
    To get the best of our technology, we recommend you to download and install the last firmware release (please refer to last page)

## Slide 32: Documentation
Documents about installing the terminal
MorphoWave Compact Installation Guide, Ref. 2018_2000035853
This document describes the terminals physical mounting procedure, electrical interfaces and connection procedures.
Documents about administrating / using the terminal
MorphoWave Compact Quick User Guide, Ref. 2018_2000035854
This document gives a quick overview of the product and the basics of configuration and use.
MorphoWave Compact Administration Guide, Ref. 2018_2000036794
This document describes the different functions available on the terminal and the procedures for configuring the terminal. It also contains the full description of all the configuration parameters for the terminal.
MorphoWave Compact Parameters Guide, Ref. 2018_2000035285
This document contains the full description of all the terminal configuration parameters.
Documents for the developer
MorphoAccess 5G Series Host System Interface Specification, Ref. 2016_2000022602
This document describes the commands supported by the MorphoAccess® terminal.
MorphoAccess 5G Series Remote Message Specification, Ref. 2016_2000022373
This document describes the format of messages sent by the terminal to a distant system.
Release note : for each firmware version, a release note is published describing the new features, the supported products, the potential known issues, the upgrade / downgrade limitations, the recommendations, the potential restrictions…

## Slide 33: Contacts
Technical Support and Hotline
North America
Mail: support.bioterminals.us@idemia.com
Tel: +1 888 940 7477
South America
Mail: support.bioterminals.us@idemia.com
Tel: +1 714 575 2973
India
Mail: support.bioterminals.in@idemia.com
Tel: 0120-4699900
For the latest firmware, software, document releases, and news, please check our website
    www.biometric-terminals.com
    To get your log in and password please contact your sales representative.
Copyright © 2018, IDEMIA. All rights reserved.
www.idemia.com
Reproduction in whole or in part in any form or medium without the express written permission of IDEMIA is prohibited.
The trademarks identified herein are the trademarks of registered trademarks of IDEMIA, or other third party.
South Africa
Mail: support.bioterminals@idemia.com
Tel: + 27 11 286 5855
Europe and rest of the world
Mail: support.bioterminals@idemia.com
Tel: +33 1 30 20 30 40
(9H00am to 5H30pm French Time, Monday to Friday)
293729933-A